Water SWAT Team Meeting

In attendance:  Jeremy Overmann, Art Schmidt, John Berens, Lauren Excell, Stephanie Cash

- BIF Greywater Meter Updates

  - Student Sustainability Committee (SSC) has recommended that the proposal for a permanent greywater meter be funded for the full $5000 requested

  - Awarded amount is retained in the SSC fee fund, however, the money must be reallocated to an organization code and program code for the unit

    - The webpage http://www.obfs.uillinois.edu/forms/accounting-financial-reporting/ will be used to apply for codes

    - Further instructions can be found in email from Micah Kenfield, SSC Coordinator

- Increase Cooling Tower COC

  - Water SWAT team will work with Campus Recreation to identity potential sites

    - Information to acquire: List of cooling towers, how many tons of cooling, year-round vs. summer operation

    - UI water from Illinois American Water which is partial softened at the plant, but has high alkalinity which can limit COC

  - Jeremy Overmann, chemist with the Institutional Water Treatment Program, reviews COC & “Zero” blowdown systems

    - COC = cycles of concentration, how many times the minerals in a batch of water gets concentrated, measured by conductivity

      - COC is controlled by choosing a rate of blowdown (where blowdown/bleed valve at bottom of tower allows fresh water to flush out the high mineral concentration water)

        - For example, water in Champaign is typically 400 microsiemens (unit of electrical conductance). If a cooling tower is run at 3 COC, the water in the tower will increase to 1200 microsiemens. Enough water will be blown into the system to keep it at that level.

      - Systems with greater COC uses less source/Make-Up water per hour, however as COC increase, the potential for calcium scale also increases (which reduces efficiency and requires labor intensive cleaning)

      - Most standard chemically treated cooling towers use unsoftened water and operate between 4-6 COC, whereas “zero” blowdown cooling towers use softened water with COC ranges from 20-100 or higher. Systems using softened water must monitor the blowdown valve (either manual or digital system). Further details and graphs can be found in email from Jeremy.

    - Champaign Regional Office Building study

      - Building owned by UI for state employees that uses 300 ton cooling tower

      - Grant from Illinois Sustainable Technology Center for research project on reducing water use

        - “Zero” blowdown cooling tower using High Efficiency Softening (HES) which softens the water before use in cooling tower (which increases COC and decreases water use from blowdown)

        - Monthly fee of $670/month to company that holds HES patent (fee covers use, inspections, wireless communication devices etc)

        - Research found this method to be economically viable if cooling plant is already running under 3 COC

        - Highest COC achieved was 51

    - Testing Lab, UI Water Stations

      - Manages closed loop heating and cooling systems

      - What is the name of this lab? Do they test water from cooling towers? Would they have suggestions for Campus Recreation cooling towers?

- Scheduling

  - Water SWAT will meet every other week on Thursdays at 4pm in the iSEE Conference Room for the remainder of the Spring 2017 semester

  - Suggestion to invite Stephanie, student clerk, to Outlook to check staff schedules

  - Schedule joint meeting with Agriculture, Land Use, Food and Sequestration (ALUF) SWATeam

  - Next meeting: Thursday, March 30th at 4p in the iSEE Conference Room

    - Moving forward with greywater design standard suggestions

    - Updates on BIF water meter